## RTU condition Data
|  |  | FY'16 | Bldg
Bldg | Building | Year | Bldg | Use | Serial # of RTU | Reference # | Model # | Make | Refrigerant | Gas Type | Cooling Capacity | Provide | Unit Configuration | Year Built | Age | Comments on Condition | Remarks
No | Name | Built | Age
36 | Reuther Library | 1974 | 41 | L | 22353-01-01 | RTU 1 |  | Mamoth | R22 (Circuit #1 -51lb, #2 -58lb) |  |  |  |  | Susp; 1990 | 26 | Poor
42 | Alumni House | 1959 | 56 | A | N22103805D | RTU 1 | TCH048C300BC | Trane | R22 (Circuit #1 -5.6lb) | N/A - Electric | 4RT | Cooling and Heating | N/A | 1998-06-01 | 18 | Fair
42 | Alumni House | 1959 | 56 | A | N22103804D | RTU 2 | TCH048C300BC | Trane | R22 (Circuit #1 -5.6lb) | N/A - Electric | 4RT | Cooling and Heating | N/A | 1998-06-01 | 18 | Fair
42 | Alumni House | 1959 | 56 | A | U02E04875 | RTU 3 | RTCA100G0F00A300AGQ | Trane | R22 | N/A | 100RT | Cooling | N/A
45 | Parking Structure #5 | 1987 | 29 | P | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
51 | Parking Structure #1 | 1966 | 50 | P | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
56 | Parking Structure #2 | 1972 | 44 | P | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
63 | 5447 Woodward and 69 West Ferry Ave | 1959 | 57 | U
74 | 95 Hancock West | 1916 | 100 | C | 3201F02928 | RTU 1 | 48TJF020 | Carrier | R22 (Circuit #1 -15.3lb, #2 -12.2lb) | Natural gas | 18RT | Cooling and Heating | N/A | N/F | N/F | Poor: Problems with fan motors and shafts
74 | 95 Hancock West | 1916 | 100 | C | 3401F06724 | RTU 2 | 48TJF024 | Carrier | R22 (Circuit #1 -16lb, #2 -13.4lb) | Natural gas | 20RT | Cooling and Heating | N/A | N/F | N/F | Poor: Problems with fan motors and shafts
74 | 95 Hancock West | 1916 | 100 | C | L022068841 | RTU 3 | PAB036N1HD | ICP -Int'l Comfort Product | R22 (Circuit #1 -6lb) | N/A - Electric | 3RT | Cooling and Heating | N/A | N/F | N/F | Poor: Problems with fan motors and shafts
74 | 95 Hancock West | 1916 | 100 | C | L022953490 | RTU 4 | PAB036N1HD | ICP -Int'l Comfort Product | R22 (Circuit #1 -6lb) | N/A - Electric | 3RT | Cooling and Heating | N/A | N/F | N/F | Poor: Problems with fan motors and shafts
78 | Stadium Auxiliary Building | 1968 | 48 | F | 437101455D | RTU 1 | TCD240B40CJB | Trane | R22 (Circuit #1 -18.9lb, #2 -21lb) | N/A - Electric | 23RT | Cooling and Heating | N/A | 2004-09-01 | 12 | Fair
78 | Stadium Auxiliary Building | 1968 | 48 | F | 436101376L | RTU 2A | YSC120A4RHA1PH1000000A200D | Trane | R22 (Circuit #1 -7.2lb, #2 -5.3lb) | Natural gas | 10RT | Cooling and Heating | N/A | 2004-09-01 | 12 | Fair
78 | Stadium Auxiliary Building | 1968 | 48 | F | 436101318L | RTU 2B | YSC120A4RHA1PH1000000A200D | Trane | R22 (Circuit #1 -7.2lb, #2 -5.3lb) | Natural gas | 10RT | Cooling and Heating | N/A | 2004-09-01 | 12 | Fair
80 | Matthaei | 1967 | 49 | F | L10103177D | AC080001 | TCD090C400BC | Trane | R22 (Circuit #1 -10.6lb, #2 -?) | N/A - Electric | 7.5RT | Cooling and Heating | N/A | 1996-03-01 | 20 | Fair
80 | Matthaei | 1967 | 49 | F | 980483 | AC080003 | E10G3A | York | R22 | N/F | 10RT | ? | N/A | Susp;1998 | 18 | Fair
80 | Matthaei | 1967 | 49 | F | N/F | AC080002 | N/F | N/F | N/F | N/F | N/F | N/F | N/F | N/F | N/F | Fair
80 | Matthaei | 1967 | 49 | F | 744102900L | AC080004 | TSC048A4E0A2B000000000000A | Trane | R22 (Circuit #1 -3.8lb) | N/A - Electric | 4RT | Cooling and Heating | N/A | 2007-11-01 | 9 | Good
80 | Matthaei | 1967 | 49 | F | 141513749L | AC080005 - New addition | THC120E4R0A0REEB0A1A000A00000E0000000000 | Trane | R410A (Circuit #1 -12.8lb, #2 -12.8lb) | N/A | 10RT | Cooling | N/A | 2014-05-01 | 2 | Very Good
83 | 60 W Hancock (ACLU Building) | 1956 | 60 | U
85 | Bookstore | 2002 | 14 | A | Old unit having problems & tripping time to time. New replacement units are ordered and in the process of delivering and installation.
87 | Parking Structure #6 (5050 Cass/Retail Unit) | 2003 | 13 | A | N0D5913447 | RTU 1 | DM120N20N4AAA3 | York | R22 (Circuit #1 -6lb, #2 -6lb) | Natural Gas | 10RT | Cooling and Heating | Air Cooled, Single Package | Susp;2003 | 13 | Fair
87 | Parking Structure #6 (5050 Cass/Retail Unit) | 2003 | 13 | A | N0A5422876 | RTU 2 | DM120N20N4AAA3 | York | R22 (Circuit #1 -6lb, #2 -6lb) | Natural Gas | 10RT | Cooling and Heating | Air Cooled, Single Package | Susp;2003 | 13 | Fair
87 | Parking Structure #6 (5050 Cass/Retail Unit) | 2003 | 13 | A | 21300 | RTU 3 | AA1-HOX | AbsolutAire | N/A | Natural Gas | N/A | Heating only | N/A | Susp;2003 | 13 | Fair
88 | Parking Structure #6 | 2001 | 15 | P | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
91 | Athletic Multi-Purpose Indoor Facility | 2011 | 5 | F | 201104-BNGX15450 | RTU 1 | RN-060-3-0-BA04-2D2 | Aaon | R410A (Circuit #1 -464oz, #2 -464oz, #3 -464oz, #4 -464oz) | Natural gas Aluminized | 60RT | Cooling and Heating | Air Cooled Cond + Std Evap. Coil | 2011-04-01 | 5 | Very Good
91 | Athletic Multi-Purpose Indoor Facility | 2011 | 5 | F | 201104-ANGJ15448 | RTU 2 | RN-010-3-0-CA01-2K2 | Aaon | R410A (Circuit #1 -328oz) | Natural gas Aluminized | 10RT | Cooling and Heating | Air Cooled Cond + Std Evap. Coil | 2011-04-01 | 5 | Very Good
104 | Atchison Residence Hall | 2003 | 13 | H | CN-3163 | RTU 1 - MUA-2 | TBA-400/DX-C15 | Air Wise - Trane | N/A | Natural gas |  | Heating | N/A | 2003-01-01 | 13 | Fair
104 | Atchison Residence Hall | 2003 | 13 | H | CN-3163 | RTU 1 - MUA-1 | TBA-400/DX-C15 | Air Wise - Trane | N/A | Natural gas |  | Heating | N/A | 2003-01-01 | 13 | Fair
115 | Yousif B Ghafari Hall | 2002 | 14 | H | CN-2561 DXC CORR 2 | RTU 1 - DXC CORR 2 | TBA-400/DX-C15 | Air Wise - Trane | N/A | Natural gas |  | Heating | N/A | 2002-05-01 | 14 | Fair
115 | Yousif B Ghafari Hall | 2002 | 14 | H | CN-2561 DXC CORR 1 | RTU 2 - DXC CORR 1 | TBA-400/DX-C15 | Air Wise - Trane | N/A | Natural gas |  | Heating | N/A | 2002-05-01 | 14 | Fair
115 | Yousif B Ghafari Hall | 2002 | 14 | H | CN-2561 DXC DINING | RTU 3 - DXC DINING | TBA-750/DX-C40 | Air Wise - Trane | N/A | Natural gas |  | Heating | N/A | 2002-05-01 | 14 | Fair
127 | Towers Residence Hall | 2005 | 11 | H | 200410-AMGP12443 | RTU 1 | 57049 RM-020-3-0-AA02-379 : L000E000EG0000B00C000000000000B | Aaon | R22 (Circuit #1 -320oz, #2 -320oz) | Natural gas Stainless Steel | 20RT | Cooling and Heating | Air Cooled Cond + Std Evap. Coil | 2004-10-01 | 12 | Good
127 | Towers Residence Hall | 2005 | 11 | H | 200410-AMGJ12436 | RTU 2 | 57048 RM-010-3-0-AA02-244 : L000E000CF0000A00C000000000000B | Aaon | R22 (Circuit #1 -144oz, #2 -144oz) | Natural gas Aluminized | 10RT | Cooling and Heating | Air Cooled Cond + Std Evap. Coil | 2004-10-01 | 12 | Good
127 | Towers Residence Hall | 2005 | 11 | H | 200410-AMGJ12435 | RTU 3 | 57048 RM-010-3-0-AA02-244 : L000E000CF0000A00C000000000000B | Aaon | R22 (Circuit #1 -144oz, #2 -144oz) | Natural gas Aluminized | 10RT | Cooling and Heating | Air Cooled Cond + Std Evap. Coil | 2004-10-01 | 12 | Good
127 | Towers Residence Hall | 2005 | 11 | H | 200410-ANGS00610 | RTU 4 | 57043 RN-026-3-0-AA02-3B9 : GEFEE00DFL0000A00C000000000000B | Aaon | R22 (Circuit #1 -216oz, #2 -216oz, #3 -216oz, #4 -216oz) | Natural gas Stainless Steel | 26RT | Cooling and Heating | Air Cooled Cond + Std Evap. Coil | 2004-10-01 | 12 | Good
127 | Towers Residence Hall | 2005 | 11 | H | 200410-ANGS00611 | RTU 5 | 57047 RN-026-3-0-AA02-3B9 : M000E00DG0000B00C000000000000B | Aaon | R22 (Circuit #1 -216oz, #2 -216oz, #3 -216oz, #4 -216oz) | Natural gas Stainless Steel | 26RT | Cooling and Heating | Air Cooled Cond + Std Evap. Coil | 2004-10-01 | 12 | Good
127 | Towers Residence Hall | 2005 | 11 | H | 200410-ANGS00611 | RTU 7 | 51034 RN-015-3-0-EB09-369 : M000U0BDRQ00A0CFAC0F000000000CX | Aaon | R410A (Circuit #1 -392oz, #2 -248oz) | Natural gas Stainless Steel | 15RT | Cooling and Heating | Air Cooled Cond + 6Row Evap. Coil | 2014-05-01 | 2 | Very Good
127 | Towers Residence Hall | 2005 | 11 | H | N/F | RTU 8 - MAU | A1-D.500-G10 | CaptiveAire | N/A | Natural gas / LP | Min/Max : 18000/197535 BTU/hr | Heating | N/F | 2014-04-01 | 2 | Very Good
130 | Faculty / Administration Building | 1990 | 26 | A | 2215U49049 | RTU 1 | 50N5HQ600B8MX8RQS4 | Carrier | R410A (Circuit #1 -71.5lb, #2 -67.9lb) | N/A | 105RT | Cooling | N/F | 2015-06-01 | 1 | Very Good
130 | Faculty / Administration Building | 1990 | 26 | A | 2315U49053 | RTU 2 | 50N5HQ6S0B8MX31282 | Carrier | R410A (Circuit #1 -71.5lb, #2 -67.9lb) | N/A | 105RT | Cooling | N/F | 2015-06-01 | 1 | Very Good
130 | Faculty / Administration Building | 1990 | 26 | A | 2415U49054 | RTU 3 | 50N5HQ6S0B8MX31282 | Carrier | R410A (Circuit #1 -71.5lb, #2 -67.9lb) | N/A | 105RT | Cooling | N/F | 2015-06-01 | 1 | Very Good
130 | Faculty / Administration Building | 1990 | 26 | A | 2215U49050 | RTU 4 | 50N5HQ600B8MX8RQS4 | Carrier | R410A (Circuit #1 -71.5lb, #2 -67.9lb) | N/A | 105RT | Cooling | N/F | 2015-06-01 | 1 | Very Good
166 | Manufacturing Engineering Building | 1996 | 20 | R | 56G8127601 | A/C 166001 | ALP070C | McQuay | R22 | N/A | 70RT | Cooling | N/F | Susp; 1996 | 20 | Fair
166 | Manufacturing Engineering Building | 1996 | 20 | R | 56G8127701 | A/C 166002 | ALP070C | McQuay | R22 | N/A | 70RT | Cooling | N/F | Susp; 1996 | 20 | Compressor tripping
167 | Engineering Technology Building | 1916 | 100 | C | J90K73303 | AC 1 - DX Cooling,No Heat, Extended Casing | SXHCC5030N45D59D3D01AGMNRTXT | Trane | R22 (49lb) | N/A | 50RT | Cooling | Air Cooled | N/F | N/F | Bad Compressor | Single Zone
167 | Engineering Technology Building | 1916 | 100 | C | J91A70410 | AC 2 - DX Cooling,No Heat, Extended Casing | SXHCC5030N67D79D3D01NRTXA | Trane | R22 (45lb) | N/A | 50RT | Cooling | Air Cooled | N/F | N/F | Fair | Single Zone
169 | Bioengineering Building | 1925 | 91 | R | J46101744D | RTU 1 | YCD103B3HCDB | Trane | R22 (Circuit #1 -7.5lb, #2 -7lb) | N/A | 9RT | Cooling and Heating | N/F | 1994-11-01 | 22 | Fair
169 | Bioengineering Building | 1925 | 91 | R | J421013B7D | RTU 2 | YCD300B3H0ODB | Trane | R22 (Circuit #1 -17lb, #2 -17lb) | N/A | 25RT | Cooling and Heating | N/F | 1994-10-01 | 22 | Dealing with some issues
169 | Bioengineering Building | 1925 | 91 | R | J46101795D | RTU 3 | YCD241B3HCDB | Trane | R22 (Circuit #1 -17.5lb, #2 -17.5lb) | N/A | 21RT | Cooling and Heating | N/F | 1994-10-01 | 22 | Refrigerant Leak
169 | Bioengineering Building | 1925 | 91 | R | J46101745D | RTU 4 | YCD103B3HCDB | Trane | R22 (Circuit #1 -7.5lb, #2 -7lb) | N/A | 9RT | Cooling and Heating | N/F | 1994-11-01 | 22 | Fair
169 | Bioengineering Building | 1925 | 91 | R | 151910403D | RTU 5 | TSD180F3R0A05D00000000000000000000000000 | Trane | R410A(Circuit #1 -11.40lb, #2 -6lb) | N/A - Electric | 15RT | Cooling and Heating | N/F | 2015-05-01 | 1 | Very Good
169 | Bioengineering Building | 1925 | 91 | R | 151910421D | RTU 6 | TSD210F3R0B07D00000000000000000000000000 | Trane | R410A(Circuit #1 -14.40lb, #2 -7.40lb) | N/A - Electric | 15RT | Cooling and Heating | N/F | 2015-05-01 | 1 | Very Good
195 | Custodial / Grounds Building | 1930 | 86 | A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
203 | 6050 Cass (WSU Police Department) | 1926 | 90 | A | 7345LWCAD | RTU 1 | TTA180B400FA | Trane - Odyssey | R22 | N/A | 15RT | Cooling | Split System Cooling | 2007-08-01 | 9 | Good
203 | 6050 Cass (WSU Police Department) | 1926 | 90 | A | 729332TAD | RTU 2 | TTA090A400FA | Trane - Odyssey | R22 | N/A | 7.5RT | Cooling | Split System Cooling | 2007-07-01 | 9 | Good
203 | 6050 Cass (WSU Police Department) | 1926 | 90 | A | C07H09360 | RTU 3 | RAUCC604BY10A00000000 | Trane | R22 | N/A | 60RT | Cooling | Air Cooled | 2016-07-07 | 9 | Good
203 | 6050 Cass (WSU Police Department) | 1926 | 90 | A | 0719N147514 | RTU for Command Center | PFH037A-YL3 | Liebert | R407C | N/A | 3RT | Cooling | Prop fan condensing unit with hot-gas bypass | 2007-01-01 | 9 | Good
203 | 6050 Cass (WSU Police Department) | 1926 | 90 | A | 0649N140167 | RTU for Command Center | PFH027A-PL3 | Liebert | R407C | N/A | 2RT | Cooling | Prop fan condensing unit with hot-gas bypass | 2006-01-01 | 10 | Good
203 | 6050 Cass (WSU Police Department) | 1926 | 90 | A | 0719N147669 | RTU for Command Center | PFH027A-PL3 | Liebert | R407C | N/A | 2RT | Cooling | Prop fan condensing unit with hot-gas bypass | 2007-01-01 | 9 | Good
217 | 1200 Holden | 1969 | 47 | A | 2214C62694 | N/F | 48TCEA07A2A5A0A0A0 | Carrier | R410A(Circuit #1 -14.2lb) | Natural gas | 6RT | Cooling and Heating | N/A | 2014-05-01 | 2 | Very Good
217 | 1200 Holden | 1969 | 47 | A | G054250794 | N/F | PGS150H250AA | ICP -Int'l Comfort Product | R22 (Circuit #1 -8.8lb, #2 -8.6lb) | Natural gas | 12.5RT | Cooling and Heating | N/A | Susp;1994 | 22 | Fair
217 | 1200 Holden | 1969 | 47 | A | 200512-AMGH22096 | N/F | 66760 RM-008-8-0AA02-339: L000E000CD0000A0AB0E0000000000B | Aaon | R22 (Circuit #1 -128oz, #2 -128oz) | Natural gas | 8RT | Cooling and Heating | N/A | 2005-12-01 | 11 | Not Working
217 | 1200 Holden | 1969 | 47 | A | 123013054L | N/F | YHC120E3RHA0JD0B00006B0A0 | Trane | R410A(Circuit #1 -14.0lb, #2 -11.8lb) | Natural gas | 10RT | Cooling and Heating | N/A | 2012-07-01 | 4 | Very Good
217 | 1200 Holden | 1969 | 47 | A | 12905101 | MAU 1 | DG-109-H10-DB | Greenheck | N/A | Natural gas | N/A | Heating only | N/A | Susp:2003 | 13 | Not Working
498 | Parking Structure #3 (Rackham Parking) | 1977 | 39 | P | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
501 | WDET Transmitter | 1996 | 20 | A
503 | 77 W Canfield (CIT Building) | 1939 | 77 | U
525 | Oakland Center | 1982 | 34 | C | J94J72735 |  | SLHFC304BE37D5CD#001AEGKRT8 | Trane |  | Natural gas | 36RT
525 | Oakland Center | 1982 | 34 | C | K94L866685 |  | PCCB-CBCGBFC0BAAB0HC4AABAFCTC0AA00000EAA00K00M00000B0LBE0CA00BEGGAAT0000000000 | Trane
527 | 1011 East Ferry Avenue | 1963 | 53 | A | STNU050600046 | Condensing Unit | ACZ025AC12-ER11 | McQuay | R22 | N/F | 25RT | Cooling | Air cooled condensing unit | N/F | N/F | N/F
527 | 1011 East Ferry Avenue | 1963 | 53 | A | N/F | RTU 1 | N/F | N/F | N/F | N/F | N/F | N/F | N/F | N/F | N/F | N/F
527 | 1011 East Ferry Avenue | 1963 | 53 | A | N/F | RTU 2 | N/F | N/F | N/F | N/F | N/F | N/F | N/F | N/F | N/F | N/F
527 | 1011 East Ferry Avenue | 1963 | 53 | A | N/F | RTU 3 | N/F | N/F | N/F | N/F | N/F | N/F | N/F | N/F | N/F | N/F
536 | Parking Structure #8 | 2008 | 8 | P | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
556 | 14601 East Twelve Mile Road (MATEC) | 1975 | 41 | C | 13524549 1401 | ERV-1 UNIT | ERV-120-30L-B | Greenheck | [8 empty] | Ventilator
556 | 14601 East Twelve Mile Road (MATEC) | 1975 | 41 | C | 14192627 | MAU 1 | IGX-115-H22-DB-10 | Greenheck
591 | Macomb Education Center | 1979 | 37 | C
595 | Parking Structure #7 | 2003 | 13 | P | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
613 | Parking Structure #4 | 1978 | 38 | P | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
992 | MCHT | 1930 | 86 | R
Abbreviations
N/A - Not applicable
N/F - Visit the place, but not found any detail
Susp; - Suspected / estimated data on available detail
Cond - Condenser
Evap - Evaporator
Std - Standard

## RTU Assesment
|  |  | FY'16 | Bldg
Bldg | Building | Year | Bldg | Use | Serial # of RTU | Reference # | Model # | Make | Refrigerant | Gas Type | Cooling Capacity | Provide | Unit Configuration | Year Built | Age | Comments on Condition | Remarks | Age FY'16 |  | Age FY'21 | Age FY'26 | Age FY'31
No | Name | Built | Age
36 | Reuther Library | 1974 | 41 | L | 22353-01-01 | RTU 1 |  | Mamoth | R22 (Circuit #1 -51lb, #2 -58lb) |  |  |  | N/A | Susp; 1990 | 26 | Poor |  | 26 | Immediate Replacement | 31 | 36 | 41
42 | Alumni House | 1959 | 56 | A | N22103805D | RTU 1 | TCH048C300BC | Trane | R22 (Circuit #1 -5.6lb) | N/A - Electric | 4RT | Cooling and Heating | N/A | 1998-06-01 | 18 | Fair
42 | Alumni House | 1959 | 56 | A | N22103804D | RTU 2 | TCH048C300BC | Trane | R22 (Circuit #1 -5.6lb) | N/A - Electric | 4RT | Cooling and Heating | N/A | 1998-06-01 | 18 | Fair
42 | Alumni House | 1959 | 56 | A | U02E04875 | RTU 3 | RTCA100G0F00A300AGQ | Trane | R22 | N/A | 100RT | Cooling | N/A
63 | 5447 Woodward and 69 West Ferry Ave | 1959 | 57 | U
74 | 95 Hancock West | 1916 | 100 | C
78 | Stadium Auxiliary Building | 1968 | 48 | F | 437101455D | RTU 1 | TCD240B40CJB | Trane | R22 (Circuit #1 -18.9lb, #2 -21lb) | N/A - Electric | 23RT | Cooling and Heating | N/A | 2004-09-01 | 12 | Fair |  | 12 | Heads Up | 17 | 22 | 27
78 | Stadium Auxiliary Building | 1968 | 48 | F | 436101376L | RTU 2A | YSC120A4RHA1PH1000000A200D | Trane | R22 (Circuit #1 -7.2lb, #2 -5.3lb) | Natural gas | 10RT | Cooling and Heating | N/A | 2004-09-01 | 12 | Fair |  | 12 | Heads Up | 17 | 22 | 27
78 | Stadium Auxiliary Building | 1968 | 48 | F | 436101318L | RTU 2B | YSC120A4RHA1PH1000000A200D | Trane | R22 (Circuit #1 -7.2lb, #2 -5.3lb) | Natural gas | 10RT | Cooling and Heating | N/A | 2004-09-01 | 12 | Fair |  | 12 | Heads Up | 17 | 22 | 27
80 | Matthaei | 1967 | 49 | F | L10103177D | AC080001 | TCD090C400BC | Trane | R22 (Circuit #1 -10.6lb, #2 -?) | N/A - Electric | 7.5RT | Cooling and Heating | N/A | 1996-03-01 | 20 | Fair |  | 20 | Attention | 25 | 30 | 35
80 | Matthaei | 1967 | 49 | F | 980483 | AC080003 | E10G3A | York | R22 | N/F | 10RT | ? | N/A | Susp;1998 | 18 | Fair |  | 18 | Attention | 23 | 28 | 33
80 | Matthaei | 1967 | 49 | F | N/F | AC080002 | N/F | N/F | N/F | N/F | N/F | N/F | N/F | N/F | N/F | Fair |  | N/F |  | N/F
80 | Matthaei | 1967 | 49 | F | 744102900L | AC080004 | TSC048A4E0A2B000000000000A | Trane | R22 (Circuit #1 -3.8lb) | N/A - Electric | 4RT | Cooling and Heating | N/A | 2007-11-01 | 9 | Good |  | 9 | No worries Live-with-it | 14 | 19 | 24
80 | Matthaei | 1967 | 49 | F | 141513749L | AC080005 - New addition | THC120E4R0A0REEB0A1A000A00000E0000000000 | Trane | R410A (Circuit #1 -12.8lb, #2 -12.8lb) | N/A | 10RT | Cooling | N/A | 2014-05-01 | 2 | Very Good |  | 2 | No worries Live-with-it | 7 | 12 | 17
83 | 60 W Hancock (ACLU Building) | 1956 | 60 | U
85 | Bookstore | 2002 | 14 | A
87 | Parking Structure #6 (5050 Cass/Retail Unit) | 2003 | 13 | A
91 | Athletic Multi-Purpose Indoor Facility | 2011 | 5 | F | 201104-BNGX15450 | RTU 1 | RN-060-3-0-BA04-2D2 | Aaon | R410A (Circuit #1 -464oz, #2 -464oz, #3 -464oz, #4 -464oz) | Natural gas Aluminized | 60RT | Cooling and Heating | Air Cooled Cond + Std Evap. Coil | 2011-04-01 | 5 | Very Good |  | 5 | No worries Live-with-it | 10 | 15 | 20
91 | Athletic Multi-Purpose Indoor Facility | 2011 | 5 | F | 201104-ANGJ15448 | RTU 2 | RN-010-3-0-CA01-2K2 | Aaon | R410A (Circuit #1 -328oz) | Natural gas Aluminized | 10RT | Cooling and Heating | Air Cooled Cond + Std Evap. Coil | 2011-04-01 | 5 | Very Good |  | 5 | No worries Live-with-it | 10 | 15 | 20
104 | Atchison Residence Hall | 2003 | 13 | H | CN-3163 | RTU 1 - MUA-2 | TBA-400/DX-C15 | Air Wise - Trane | N/A | Natural gas |  | Heating | N/A | 2003-01-01 | 13 | Fair |  | 13 | Heads Up | 18 | 23 | 28
104 | Atchison Residence Hall | 2003 | 13 | H | CN-3163 | RTU 1 - MUA-1 | TBA-400/DX-C15 | Air Wise - Trane | N/A | Natural gas |  | Heating | N/A | 2003-01-01 | 13 | Fair |  | 13 | Heads Up | 18 | 23 | 28
115 | Yousif B Ghafari Hall | 2002 | 14 | H | CN-2561 DXC CORR 2 | RTU 1 - DXC CORR 2 | TBA-400/DX-C15 | Air Wise - Trane | N/A | Natural gas |  | Heating | N/A | 2002-05-01 | 14 | Fair |  | 14 | Heads Up | 19 | 24 | 29
115 | Yousif B Ghafari Hall | 2002 | 14 | H | CN-2561 DXC CORR 1 | RTU 2 - DXC CORR 1 | TBA-400/DX-C15 | Air Wise - Trane | N/A | Natural gas |  | Heating | N/A | 2002-05-01 | 14 | Fair |  | 14 | Heads Up | 19 | 24 | 29
115 | Yousif B Ghafari Hall | 2002 | 14 | H | CN-2561 DXC DINING | RTU 3 - DXC DINING | TBA-750/DX-C40 | Air Wise - Trane | N/A | Natural gas |  | Heating | N/A | 2002-05-01 | 14 | Fair |  | 14 | Heads Up | 19 | 24 | 29
127 | Towers Residence Hall | 2005 | 11 | H | 200410-AMGP12443 | RTU 1 | 57049 RM-020-3-0-AA02-379 : L000E000EG0000B00C000000000000B | Aaon | R22 (Circuit #1 -320oz, #2 -320oz) | Natural gas Stainless Steel | 20RT | Cooling and Heating | Air Cooled Cond + Std Evap. Coil | 2004-10-01 | 12 | Good |  | 12 | Heads Up | 17 | 22 | 27
127 | Towers Residence Hall | 2005 | 11 | H | 200410-AMGJ12436 | RTU 2 | 57048 RM-010-3-0-AA02-244 : L000E000CF0000A00C000000000000B | Aaon | R22 (Circuit #1 -144oz, #2 -144oz) | Natural gas Aluminized | 10RT | Cooling and Heating | Air Cooled Cond + Std Evap. Coil | 2004-10-01 | 12 | Good |  | 12 | Heads Up | 17 | 22 | 27
127 | Towers Residence Hall | 2005 | 11 | H | 200410-AMGJ12435 | RTU 3 | 57048 RM-010-3-0-AA02-244 : L000E000CF0000A00C000000000000B | Aaon | R22 (Circuit #1 -144oz, #2 -144oz) | Natural gas Aluminized | 10RT | Cooling and Heating | Air Cooled Cond + Std Evap. Coil | 2004-10-01 | 12 | Good |  | 12 | Heads Up | 17 | 22 | 27
127 | Towers Residence Hall | 2005 | 11 | H | 200410-ANGS00610 | RTU 4 | 57043 RN-026-3-0-AA02-3B9 : GEFEE00DFL0000A00C000000000000B | Aaon | R22 (Circuit #1 -216oz, #2 -216oz, #3 -216oz, #4 -216oz) | Natural gas Stainless Steel | 26RT | Cooling and Heating | Air Cooled Cond + Std Evap. Coil | 2004-10-01 | 12 | Good |  | 12 | Heads Up | 17 | 22 | 27
127 | Towers Residence Hall | 2005 | 11 | H | 200410-ANGS00611 | RTU 5 | 57047 RN-026-3-0-AA02-3B9 : M000E00DG0000B00C000000000000B | Aaon | R22 (Circuit #1 -216oz, #2 -216oz, #3 -216oz, #4 -216oz) | Natural gas Stainless Steel | 26RT | Cooling and Heating | Air Cooled Cond + Std Evap. Coil | 2004-10-01 | 12 | Good |  | 12 | Heads Up | 17 | 22 | 27
127 | Towers Residence Hall | 2005 | 11 | H | 200410-ANGS00611 | RTU 7 | 51034 RN-015-3-0-EB09-369 : M000U0BDRQ00A0CFAC0F000000000CX | Aaon | R410A (Circuit #1 -392oz, #2 -248oz) | Natural gas Stainless Steel | 15RT | Cooling and Heating | Air Cooled Cond + 6Row Evap. Coil | 2014-05-01 | 2 | Very Good |  | 2 | No worries Live-with-it | 7 | 12 | 17
127 | Towers Residence Hall | 2005 | 11 | H | N/F | RTU 8 - MAU | A1-D.500-G10 | CaptiveAire | N/A | Natural gas / LP | Min/Max : 18000/197535 BTU/hr | Heating | N/F | 2014-04-01 | 2 | Very Good |  | 2 | No worries Live-with-it | 7 | 12 | 17
130 | Faculty / Administration Building | 1990 | 26 | A | 2215U49049 | RTU 1 | 50N5HQ600B8MX8RQS4 | Carrier | R410A (Circuit #1 -71.5lb, #2 -67.9lb) | N/A | 105RT | Cooling | N/F | 2015-06-01 | 1 | Very Good |  | 1 | No worries Live-with-it | 6 | 11 | 16
130 | Faculty / Administration Building | 1990 | 26 | A | 2315U49053 | RTU 2 | 50N5HQ6S0B8MX31282 | Carrier | R410A (Circuit #1 -71.5lb, #2 -67.9lb) | N/A | 105RT | Cooling | N/F | 2015-06-01 | 1 | Very Good |  | 1 | No worries Live-with-it | 6 | 11 | 16
130 | Faculty / Administration Building | 1990 | 26 | A | 2415U49054 | RTU 3 | 50N5HQ6S0B8MX31282 | Carrier | R410A (Circuit #1 -71.5lb, #2 -67.9lb) | N/A | 105RT | Cooling | N/F | 2015-06-01 | 1 | Very Good |  | 1 | No worries Live-with-it | 6 | 11 | 16
130 | Faculty / Administration Building | 1990 | 26 | A | 2215U49050 | RTU 4 | 50N5HQ600B8MX8RQS4 | Carrier | R410A (Circuit #1 -71.5lb, #2 -67.9lb) | N/A | 105RT | Cooling | N/F | 2015-06-01 | 1 | Very Good |  | 1 | No worries Live-with-it | 6 | 11 | 16
166 | Manufacturing Engineering Building | 1996 | 20 | R | 56G8127601 | A/C 166001 | ALP070C | McQuay | R22 | N/A | 70RT | Cooling | N/F | Susp; 1996 | 20 | Fair |  | 20 | Attention | 25 | 30 | 35
166 | Manufacturing Engineering Building | 1996 | 20 | R | 56G8127701 | A/C 166002 | ALP070C | McQuay | R22 | N/A | 70RT | Cooling | N/F | Susp; 1996 | 20 | Compressor tripping |  | 20 | Attention | 25 | 30 | 35
167 | Engineering Technology Building | 1916 | 100 | C | J90K73303 | AC 1 - DX Cooling,No Heat, Extended Casing | SXHCC5030N45D59D3D01AGMNRTXT | Trane | R22 (49lb) | N/A | 50RT | Cooling | Air Cooled |  |  | Bad Compressor | Single Zone
167 | Engineering Technology Building | 1916 | 100 | C | J91A70410 | AC 2 - DX Cooling,No Heat, Extended Casing | SXHCC5030N67D79D3D01NRTXA | Trane | R22 (45lb) | N/A | 50RT | Cooling | Air Cooled |  |  | Fair | Single Zone
169 | Bioengineering Building | 1925 | 91 | R | J46101744D | RTU 1 | YCD103B3HCDB | Trane | R22 (Circuit #1 -7.5lb, #2 -7lb) | N/A | 9RT | Cooling and Heating | N/F | 1994-11-01 | 22 | Fair |  | 22 | Attention | 27 | 32 | 37
169 | Bioengineering Building | 1925 | 91 | R | J421013B7D | RTU 2 | YCD300B3H0ODB | Trane | R22 (Circuit #1 -17lb, #2 -17lb) | N/A | 25RT | Cooling and Heating | N/F | 1994-10-01 | 22 | Dealing with some issues |  | 22 | Attention | 27 | 32 | 37
169 | Bioengineering Building | 1925 | 91 | R | J46101795D | RTU 3 | YCD241B3HCDB | Trane | R22 (Circuit #1 -17.5lb, #2 -17.5lb) | N/A | 21RT | Cooling and Heating | N/F | 1994-10-01 | 22 | Refrigerant Leak |  | 22 | Attention | 27 | 32 | 37
169 | Bioengineering Building | 1925 | 91 | R | J46101745D | RTU 4 | YCD103B3HCDB | Trane | R22 (Circuit #1 -7.5lb, #2 -7lb) | N/A | 9RT | Cooling and Heating | N/F | 1994-11-01 | 22 | Fair |  | 22 | Attention | 27 | 32 | 37
169 | Bioengineering Building | 1925 | 91 | R | 151910403D | RTU 5 | TSD180F3R0A05D00000000000000000000000000 | Trane | R410A(Circuit #1 -11.40lb, #2 -6lb) | N/A - Electric | 15RT | Cooling and Heating | N/F | 2015-05-01 | 1 | Very Good |  | 1 | No worries Live-with-it | 6 | 11 | 16
169 | Bioengineering Building | 1925 | 91 | R | 151910421D | RTU 6 | TSD210F3R0B07D00000000000000000000000000 | Trane | R410A(Circuit #1 -14.40lb, #2 -7.40lb) | N/A - Electric | 15RT | Cooling and Heating | N/F | 2015-05-01 | 1 | Very Good |  | 1 | No worries Live-with-it | 6 | 11 | 16
195 | Custodial / Grounds Building | 1930 | 86 | A
203 | 6050 Cass (WSU Police Department) | 1926 | 90 | A | 7345LWCAD | RTU 1 | TTA180B400FA | Trane - Odyssey | R22 | N/A | 15RT | Cooling | Split System Cooling | 2007-08-01 | 9 | Good |  | 9 | No worries Live-with-it | 14 | 19 | 24
203 | 6050 Cass (WSU Police Department) | 1926 | 90 | A | 729332TAD | RTU 2 | TTA090A400FA | Trane - Odyssey | R22 | N/A | 7.5RT | Cooling | Split System Cooling | 2007-07-01 | 9 | Good |  | 9 | No worries Live-with-it | 14 | 19 | 24
203 | 6050 Cass (WSU Police Department) | 1926 | 90 | A | C07H09360 | RTU 3 | RAUCC604BY10A00000000 | Trane | R22 | N/A | 60RT | Cooling | Air Cooled | 2007-07-01 | 9 | Good |  | 9 | No worries Live-with-it | 14 | 19 | 24
203 | 6050 Cass (WSU Police Department) | 1926 | 90 | A | 0719N147514 | RTU for Command Center | PFH037A-YL3 | Liebert | R407C | N/A | 3RT | Cooling | Prop fan condensing unit with hot-gas bypass | 2007-01-01 | 9 | Good |  | 9 | No worries Live-with-it | 14 | 19 | 24
203 | 6050 Cass (WSU Police Department) | 1926 | 90 | A | 0649N140167 | RTU for Command Center | PFH027A-PL3 | Liebert | R407C | N/A | 2RT | Cooling | Prop fan condensing unit with hot-gas bypass | 2006-01-01 | 10 | Good |  | 10 | Heads Up | 15 | 20 | 25
203 | 6050 Cass (WSU Police Department) | 1926 | 90 | A | 0719N147669 | RTU for Command Center | PFH027A-PL3 | Liebert | R407C | N/A | 2RT | Cooling | Prop fan condensing unit with hot-gas bypass | 2007-01-01 | 9 | Good |  | 9 | No worries Live-with-it | 14 | 19 | 24
217 | 1200 Holden | 1969 | 47 | A
498 | Parking Structure #3 (Rackham Parking) | 1977 | 39 | P
501 | WDET Transmitter | 1996 | 20 | A
503 | 77 W Canfield (CIT Building) | 1939 | 77 | U
525 | Oakland Center | 1982 | 34 | C
527 | 1011 East Ferry Avenue | 1963 | 53 | A
536 | Parking Structure #8 | 2008 | 8 | P
556 | 14601 East Twelve Mile Road (MATEC) | 1975 | 41 | C
591 | Macomb Education Center | 1979 | 37 | C
595 | Parking Structure #7 | 2003 | 13 | P
613 | Parking Structure #4 | 1978 | 38 | P
992 | MCHT | 1930 | 86 | R
NOTES :
ALL THE RISK/CONDITION ASSESSMENTS OF THE EQUIPMENT ARE BASED ON: ACCORDING TO THE "ASHRAE" EQUIPMENT LIFE EXPECTANCY CHART (refer: www.ashrae.org) ROOF-TOP AIR CONDITIONERS SINGLE-ZONE/MULTI-ZONE IS 15 YERS (meadian) COILS - DX / AIR COOLED CONDENSERS ARE 20 YEARS (meadian)
Replacement expirience and decision of Reuther Library and Book Store RTUs are considered as model examples