Facilities Planning and Management

Design Services

Results of Meeting with Bureau of Fire Services (BFS) in Lansing

June 18, 2007

Revised July 17, 2007

Present:          Brian Williams, Code Specialist

Randy Paquette, Director

Fran Ahern, Assistant Director

Finding Information:

www.michigan.gov/bfs

Public Act 1941 Act 207

Definition of Classroom and Classroom Building- look under Administrative Rules

Download application form

Responsible people at Bureau of Fire Safety:

Fire alarm		Roy Stelamaki

Fire suppression		Don Welch

Plan Reviewer 		Brian Williams

Submission of Documents:

All Classroom and Dormitory buildings.

Documents must be sign and sealed by a licensed architect when construction cost estimated in excess of $15K.  If less than $15K does not require a sealed document submission but documents still must be submitted to the Fire Marshal.

Documents must be submitted for projects in classroom and dormitory buildings that are as simple as dividing a larger room to make two; install a new door  into a corridor; relocation of a fire alarm device; altering an exit route; changing a ceiling; etc.

We need to review the language of a plan review application for accuracy before sending to state.  On smaller projects above $15K (not major multi million dollar work) WSU will submit the application to the Fire Marshal after the architect has filled out the form.  (This would have prevented confusion on a recent project submission.)

Important to review with Fran when classroom or dorm project is planned.

This will cause delays to the typical schedule.

Redecorating:  which does not need to be submitted to the Fire Marshal.

When work being done is replacing like with like such as carpet with carpet.

Exception:  When replacing ceilings documents must be submitted to the Fire Marshal.

No value cap on work being completed.

Mixed Occupancy Buildings:

Review only portions of building that represent classroom or dormitory.  Two (2) hour separation required to delineate.  Try to get head end fire alarm and fire suppression system in the “non-classroom” portion.  Then only terminal devices and branches are reviewed.  Permits for fire alarm and fire suppression should be acquired unless they, too are separated along the building separation.

State Permits for Construction:

Mechanical, Electrical, and Plumbing permits and inspections continue to be required.  The contractor applies for these.  No plan review needed by the Bureau of Construction Codes.

Early work packages for CM work and  Phased Construction:

Do not submit foundation and structural plans separately for fast track project.  Submit plans and fees when 100% of the construction documentation (including interiors package) is finalized. (In the future, BFS construction process will be amended to permit early footing/foundation bid packs.)

Phased occupancy should have phased fire alarm and fire protection drawings.  BFS will not approve partial occupancy if full system drawings were submitted and approved.  The have no mechanism for partial occupancy approval under these conditions.

Other Comments:

The Farmington Hills office handles our inspections.  Inspectors are rotated periodically so we may not see the same inspector.

Make sure that you have include plan review fees in your financial summary spreadsheet.  On large multi million dollar projects these fees are substantial. ($30m cost of work = $60,000 fee)

Fire Marshal will only review on state owned & lease buildings when DMB requests.

State approval for fire alarm systems and fire suppression systems in non-state authority buildings is unclear at this time.

/tmp/in/input.doc